## Heating System (Winter Conditio
System Component | Option 1 | Option 2 | Option 3 | Notes/Comments
Production Type | Mixed heating-DHW system | Mixed heating-DHW system | Mixed heating-DHW system | Shared production for heating and domestic hot water
Energy Source | Biomass pellets | Biomass pellets | Biomass pellets | Renewable energy source
Boiler Type | Individual biomass boiler | Individual biomass boiler | Individual biomass boiler | -
Rated Power | 25 kW | 25 kW | 25 kW | Thermal power
Efficiency | 93% | 93% | 93% | At nominal power
Distribution | Water circuit | Water circuit | Water circuit | Supply temperature: 45°C
Emitters | Radiant floor | Radiant floor | Radiant floor | Low temperature system
Power Density - Ground Floor | 70 W/m² | 70 W/m² | 70 W/m² | -
Power Density - Attic Floor | Not applicable | 85 W/m² | 85 W/m² | Option 1 has no attic
Total Heating Power | 4.48 kW | 5.84 kW | 8.56 kW | Calculated from room distributions
4480

## Cooling System (Summer Conditio
Parameter | Value | Notes/Comments
Active Cooling System | None proposed | Due to low cooling demands in E1 climate zone
Default HULC System | Electric | Used for simulation purposes only
Nominal Efficiency | 2.6 | Default system performance
Energy Vector | Electricity | -

## Domestic Hot Water (DHW) System
Parameter | Option 1 | Option 2 | Option 3 | Notes/Comments
Production | Biomass boiler | Biomass boiler | Biomass boiler | Shared with heating system
Storage Tank | 100 liters | 100 liters | 150 liters | Larger tank for higher demand
Distribution Temperature | 60°C | 60°C | 60°C | Service temperature
Utilization Temperature | 60°C | 60°C | 60°C | -
Bedrooms | 1 | 2 | 3 | Determines occupancy
Occupants | 1.5 | 3 | 4 | Based on DB HE standards
DHW Needs per person | 28 l/person/day | 28 l/person/day | 28 l/person/day | Standard consumption
Total Daily Demand | 42 l/day | 84 l/day | 112 l/day | Calculated demand

## Ventilation System (Option 1)
Parameter | Value | Notes/Comments
System Type | Hybrid ventilation | Natural admission + mechanical extraction
Admission - Dry Rooms | 14 l/s | Bedroom: 8 l/s, Living-dining: 6 l/s
Extraction - Wet Rooms | 12 l/s | Kitchen: 6 l/s, Bathroom: 6 l/s
Minimum Extraction | 12 l/s | -
Balanced Reference Flow | 14 l/s (50.4 m³/h) | -
Equipment | 1 multi-tube extractor | -
Extractor Power | 5 W | - | 0.099206 | W/(m^3/h)
Max Flow per Extractor | 75 m³/h | -

## Ventilation System (Option (2)
Parameter | Value | Notes/Comments
System Type | Hybrid ventilation | Natural admission + mechanical extraction
Admission - Dry Rooms | 20 l/s | Master bedroom: 8 l/s, Bedroom 2: 4 l/s, Living-dining: 8 l/s
Extraction - Wet Rooms | 21 l/s | Kitchen: 7 l/s, Bathroom GF: 7 l/s, Bathroom attic: 7 l/s
Minimum Extraction | 24 l/s | -
Balanced Reference Flow | 24 l/s (86.4 m³/h) | -
Equipment | 2 multi-tube extractors | -
Extractor Power | 4 W each | -
Max Flow per Extractor | 50 m³/h | -

## Ventilation System (Option (3)
Parameter | Value | Notes/Comments
System Type | Hybrid ventilation | Natural admission + mechanical extraction
Admission - Dry Rooms | 33 l/s | Master: 8 l/s, Bed2: 4 l/s, Bed3: 4 l/s, Living-dining: 8 l/s, Attic living: 9 l/s
Extraction - Wet Rooms | 32 l/s | Kitchen: 8 l/s, 3 bathrooms: 8 l/s each
Minimum Extraction | 33 l/s | -
Balanced Reference Flow | 33 l/s (118.8 m³/h) | -
Equipment | 2 multi-tube extractors | -
Extractor Power | 5 W each | -
Max Flow per Extractor | 75 m³/h | -